## Calculator
THEORETICAL CALCULATOR (USING 0.1 BAR LOSS PER M)
BASE PUMP AT 10 BARS 400 l/m required at Branch
NOTIONAL HEIGHT OF EACH FLOOR |  |  | 2 | Meters
HEIGHT OF LOBBY |  |  | 3 | Meters
NUMBER OF FLOORS ABOVE LOBBY |  |  | 10
SB Nozzle Diameter (mm) |  |  | 11 | Millimeters
Effective height |  |  | 23
Effective pressure loss through Head |  |  | 2.3
Resultant pressure at Outlet |  |  | 7.7
Flow rate (Mid Matic) |  | Loss @ 400lpm | Output Bar |  | Midmatic req 5 Bar
1 length 45 |  | 1 | 6.7 |  | inlet pressure to flow
2 length 45 |  | 2 | 5.7 |  | minimum 400 lpm
3 length 45 |  | 3 | 4.7
Flow rate (Mid Matic) |  | Loss @ 400lpm | Output Bar
1 length 51 |  | 0.5 | 7.2
2 length 51 |  | 1 | 6.7
3 length 51 |  | 1.5 | 6.2
Flow rate (SB) |  | Loss @ 400lpm | Output Bar | Flow | JR (N)
1 length 45 |  | 1 | 5.7 | 192.6853 | 108.2829
2 length 45 |  | 2 | 4.7 | 174.9686 | 89.2859
3 length 45 |  | 3 | 3.7 | 155.243 | 70.2889
Flow rate (SB) |  | Loss @ 400lpm | Output Bar | Flow | JR (N)
1 length 51 |  | 0.5 | 6.2 | 200.9588 | 117.7814
2 length 51 |  | 1 | 5.7 | 192.6853 | 108.2829
3 length 51 |  | 1.5 | 5.2 | 184.0403 | 98.7844